## CUSTOMER INFO
Email complete form to MWS.DS@nashville.gov
REQUEST DATE :
DEVELOPMENT NAME:
DEVELOPMENT ADDRESS:
APN (if applicable):
CONTACT PERSON :
EMAIL :
COMPANY NAME :
COMPANY ADDRESS :
CITY : |  |  | STATE : |  | ZIP :
PHONE :
COMMENTS:
REQUEST TO BE ON SITE:
PURPOSE OF HYDRANT TEST (CHECK ALL THAT APPLY):
REVIEW FOR BUILDING PERMIT REQUIRED BY:
|  | Flow Requirement |  |  |  | GPM
ENGINEER/FIRE SPRINKLER COMPANY
Proposed tap location(s) & main size:
Proposed tap location(s) & main size:
PERMIT # (WSFH):
WORK ORDER #:
DATE OF TEST:
TIME OF TEST:
FLOW HYD ADDRESS:
FLOW HYD ID:
MONITOR HYD ADDRESS:
MONITOR HYD ID:
COMMENTS:
|  |  |  | CHARGES : |  | 350
MWS INITIALS: |  |  |  | Plus 10% Tech Fee per BL2022-1254
rev02132026smr |  |  |  | TOTAL : |  | 385
HYDRANT FLOW TEST
CUSTOMER INFORMATION AND BILLING SUMMARY FORM
Fire Marshal
Metro Water Services
Sprinkler Design
CUSTOMER INFORMATION
NO
YES
FOR METRO WATER SERVICES USE ONLY
Proposed Development with Hydrants

## TEST FORM-RESULTS
Two Hydrant Test Results Summary
System Services Division (SSD)
[7 empty] | Business Unit: 65556810 Work Order # | 0
Date of Test |  | 0 |  |  |  | Request Date: | 0
Property Location |  | 0
Cross Street: |  | 0
Hydrant # 1 - Flowing Hydrant
MWS ID |  | 0
Static Pressure |  |  | psi | Time ON
Flow Pressure (Pitot) |  |  | psi | Time OFF
Hydrant Outlet Coefficient |  |  | 0.9
Hydrant Outlet Diameter |  |  | 2.5 | inches
This corresponds to a flowrate of |  |  | 0 | gpm | Using the Orifice Eqtn. (4.7.3 of NFPA 291)
Hydrant #2 - Monitoring Hydrant
MWS ID |  | 0
Static Pressure |  |  | psi | Time ON
Residual Pressure |  |  | psi | Time OFF
Calculation of available fire flow at 20 psi as required by Table H.5.1 of the NFPA 1 Uniform Fire Code 2006 Edition (Using the pressure relational equation - 4.10.1.2 of NFPA 291)
With a 20 psi residual pressure at Hydrant #2, the available flow in the main at Hydrant #1 is: | [6 empty] | Review | gpm
MWS is providing these instantaneous readings for informational purposes only and cannot ensure that it represents actual hydrant flow conditions over any period of time.
Residual Presure at Hydrant #2 (psi) | Flow (gpm)
5 | #NUM!
10 | #NUM!
15 | #NUM!
20 | #NUM!
25 | #NUM!
30 | #NUM!
35 | #NUM!
40 | #NUM!
45 | #NUM!
50 | #NUM!
55 | #NUM!
60 | #NUM!
65 | #NUM!
70 | #NUM!
75 | #NUM!
80 | #NUM!
85 | #NUM!
90 | #NUM!
95 | #NUM!
100 | #NUM!
105 | #NUM!
110 | #NUM!
115 | #NUM!
120 | #NUM!
125 | #NUM!
130 | #NUM!
135 | #NUM!
140 | #NUM!
145 | #NUM!
150 | #NUM!